## Sheet1
Diagnostic | Code Message | Note
code | AFDD-1 (Temperature Sensor Fault)
20 | No faults detected
21 | Temperature sensor fault | The passive diagnostic does not deterimine which temperature sensor is faulty.
22 | Conditions not favorable for diagnostic
23 | Mixed-air temperature outside of expected range
24 | Return-air temperature outside of expected range
25 | Outside-air temperature outside of expected range
29 | Unit is off (No Fault)
AFDD-2 (Unit Not Economizing When it Should)
30 | No faults detected
31 | Unit is not currently cooling (No Fault)
32 | Economizer type is not properly configured (No Fault)
33 | Conditions are not favorable for economizing (No Fault)
32 | Insufficient outdoor air when economizing (Fault)
34 | Outdoor-air damper is not fully open when the unit should be economizing (Fault) | Unit is not fully utilizing economzing or a mechanical issue is causing outdoor-air fraction to be too low.
35 | OAD is open but conditions were not favorable for OAF calculation (No Fault) | Mixed-air temperature (MAT) is not trended and the heating or cooling is active. Since discharge-air temperature (DAT) is used instead of MAT the heating and cooling cannot be active (unfavorable condition).
36 | OAD is open when economizing but OAF calculation led to an unexpected value (No Fault) | OAF calculation is not in the range of [0,1.25]
39 | Unit is off (No Fault)
AFDD-3 (Unit Economizing When it Should Not)
40 | No faults detected
41 | Economizer type is not properly configured (No Fault)
42 | Conditions favorable for economizing (No Fault) | Since some units utilize integrated economizer logic and only the compressor command is known a unit maybe in a cooling mode and economizing when the compressor is off.
43 | Damper should be at minimum position but is not (Fault)
49 | Unit is off (No Fault)
AFDD-4 (Excess Outdoor-air Intake)
50 | No faults detected
52 | Unit should be economizing (No Fault)
53 | Damper is not at minimum (Fault)
54 | Damper is at minimum but conditions are not favorable for OAF calculation (No Fault)
55 | Damper is at minimum but OAF calculation led to an unexpected value (No Fault) | OAF calculation is not in the range of [0,1.25]
56 | Excessive outdoor-air intake (Fault)
59 | Unit is off (No Fault)
AFDD-5 (Insufficient Outdoor-air Ventilation)
60 | No faults detected
61 | Damper is below the the minimum position.
62 | Damper is at minimum but conditions are not favorable for OAF calculation (No Fault) | The difference of the outdoor-air temperature and mixed-air temperature should be at least 5F for OAF calculation.
63 | Insufficient outdoor-air intake (Fault)
68 | Damper is at minimum but OAF calculation led to an unexpected value (No Fault) | OAF calculation is not in the range of [0,1.25]
69 | Unit is off (No Fault)
AFDD-6 (Schedule)
70 | Unit is operating correctly based on input on/off time (No Fault)
71 | Unit is operating at a time designated in schedule as "off" time